## Aspect # 1
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 1: Fire alarm system/devices
Device | main alarm panel | annunciator panels | manual pull station | manual pull station-2stage | smoke detector | smoke detector | heat detector RHT | pressure switch | flow switch | Supervisory device | strobe | horn with strobe | buzzer/chime/audible device | bell | fault isolation module/iso | end of line resistor
Type |  |  |  |  | duct | photo or ion | rate of rise | low air |  | other
BUILDING | Make/Stage | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty
A | 1 - Simplex 4100U - 1 stage | 1 | 2 | 6 | 2 | 8 |  |  | 7 | 2 | 1 |  |  | 8 |  | 2
B | 1 - Simplex 4010 - 1 stage | 1 |  | 7 | 3 | 3 |  |  | 3 | 7 | 3 |  |  | 9 |  | 1
C | 1 - Simplex 4010 - 1 stage |  |  | 4 | 9 | [8 empty] | 1 |  | 1
D | 1 - Simplex 4010 - 1 stage | 2 |  | 3 |  | 27 |  |  | 1 | 1 | 2 |  | 13 | 3 |  | 1
E | 1 - Simplex 4010 - 2 stage | 1 |  | 5 | 3 | 23 |  | 1 | 7 | 10 | 1 | 3 | 1 | 11 |  | 2
F | 1 - Simplex 4010 ES - 2 stage |  | 18 |  | 10 | 8 |  |  | 6 | 15 | 2 |  |  | 6 |  | 2
G | 1 - Simplex 4010 - 1 stage |  |  | 3 |  | 10 |  |  | 1 | 2 | 2 |  | 1 | 3 |  | 1
H | 1 - Simplex 4010 - 1 stage |  | 3 |  |  | 2 | 4 |  |  | 2 |  |  |  | 2 |  | 1
J | 1 - Simplex 4010 - 1 stage |  |  | 5 |  |  | 14 | [6 empty] | 3 |  | 2
K | 1 - Simplex 4010 - 1 stage |  | 3 |  |  | 6 | [7 empty] | 1 |  | 1
L | 1 - Simplex 4010 - 1 stage |  | 2 |  |  |  | 5 | [6 empty] | 1
P | 1 - Simplex 4010 - 1 stage |  | 4 |  | 2 | 3 |  |  | 1 | 3 |  |  |  | 4 |  | 1
Q | 1 - Simplex 4100 ES - 1 stage |  | 10 |  |  | 4 |  |  | 3 | 7 |  |  |  | 7 |  | 2
R | 1 - Simplex 4100 ES - 1 stage | 1 |  | 12 |  | 41 |  |  | 4 | 9 |  | 16 | 9 |  |  | 1
Housing 01 | 1 - Simplex 4010 ES - 2 stage |  |  | 3 |  | 8 |  |  | 1 | 1 | 2 |  |  | 2 | 3 | 1
Housing 02 | 1 - Simplex 4010 ES - 2 stage |  | 1 | 3 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 03 | 1 - Simplex 4010 ES - 2 stage |  |  | 4 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 04 | 1 - Simplex 4010 ES - 2 stage |  |  | 4 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 05 | 1 - Simplex 4010 ES - 2 stage |  |  | 5 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 06 | 1 - Simplex 4010 ES - 2 stage |  |  | 5 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 07 | 1 - Simplex 4002 - 2 stage |  |  | 5 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 08 | 1 - Simplex 4010 ES - 2 stage |  |  | 5 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 09 | 1 - Simplex 4010 ES - 2 stage |  |  | 5 |  | 8 |  |  | 1 | 1 |  |  |  | 2 | 3 | 1
Housing 10 | 1 - Simplex 4010 - 1 stage |  | 4 |  |  | 10 |  |  | 2 | 4 |  |  |  | 3 |  | 1
Housing 11 | 1 - Simplex 4010 - 1 stage |  | 3 |  |  | 10 |  |  | 2 | 2 |  |  |  | 3 |  | 1
TOTAL | 25 | 6 | 50 | 84 | 29 | 227 | 23 | 1 | 46 | 73 | 13 | 14 | 24 | 83 | 27 | 29

## Aspect # 2
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 2: Sprinkler systems/trees
Component | Dry sprinkler system | Wet sprinkler system | Pre action system | flow valve (supy) | shut off/isolation valve | Fire Dept connections
BUILDING | Qty | Qty | Qty | Qty | Qty | Qty
A |  | 2 | 2 | 8 | 5 | 1
B |  | 3 |  | 3 | 4 | 1
D |  | 1 |  |  | 1 | 1
E |  | 6 |  | 6 | 9
F | 2 | 3 |  | 2 | 7 | 1
G |  | 1 |  | 1 | 2
P |  | 1 |  | 1 | 1 | 1
Q |  | 2 |  | 2 | 5 | 1
R |  | 4 |  | 4 | 7 | 1
Housing 01 |  | 1 |  | 1 | 1
Housing 02 |  | 1 |  | 1 | 1
Housing 03 |  | 1 |  | 1 | 1
Housing 04 |  | 1 |  | 1 | 1
Housing 05 |  | 1 |  | 1 | 1
Housing 06 |  | 1 |  | 1 | 1
Housing 07 |  | 1 |  | 1 | 1
Housing 08 |  | 1 |  | 1 | 1
Housing 09 |  | 1 |  | 1 | 1
Housing 10 |  | 2 |  | 2 | 4
Housing 11 |  | 2 |  | 2 | 2
TOTALS | 2 | 36 | 2 | 40 | 56 | 7
Total # of gauges on site for each type of sprinkler system | 2 | 65 | 2

## Aspect # 3
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 3: Emergency Lighting
BUILDING | Location | Make | Watts | # of remote heads
A | front office ar2 | Ready-Lite | 560 | 6
A | file vault ar54 | Stanpro | 720 | 12
A | mccp | Ready-Lite | 360 | 2
A | elec rm | Stanpro SLA-2L | 360 | 7
B | kitchen br18 | Stanpro SLA-2L | 360 | 8
B | pw office br9 | Stanpro SLA-2L | 360 | 6
B | elec rm | Stanpro | 560 | 8
C | main by washroom | Ready-Lite | 100 | 4
C | elec rm | Ready-Lite | 100 | 5
D | rm 121 | Beghelli | 100 | 0
D | mech rm | Ready-Lite | 200 | 3
E | elec rm-office/attics/mech | Ready-Lite | 720 | 9
E | elec rm - east/west/wings | Ready-Lite | 560 | 2
E | elec rm-south wing mech | Ready-Lite | 560 | 8
F | lobby-in front of imo station | Stanpro SLA-2L | 150 | 0
F | lobby-in front of imo station | Stanpro SLA-2L | 150 | 0
F | lobby - imo station | Stanpro SLA-2L | 150 | 0
F | case management | Stanpro SLA-2L | 150 | 0
F | case management | Stanpro SLA-2L | 150 | 0
F | case management | Stanpro SLA-2L | 150 | 0
F | prog-chaplin fr-35 | Stanpro SLA-2L | 150 | 0
F | prog-elec rm fr-12 | Stanpro SLA-2L | 560 | 18
H | gen rm west wall | Luma-cell | 150 | 0
J | by washroom | Stanpro SLA-2L |  | 3
J | kitchen | Stanpro SLA-2L |  | 2
K | by storage rm | Ready-Lite | 100 | 3
K | elec rm | Ready-Lite | 100 | 0
L | works -shop | Luma-cell | 144 | 5
P | elec rm | Ready-Lite | 200 | 5
Q | iss/mech/&fire | Ready-Lite | 200 | 7
Q | office/upstairs | Ready-Lite | 200 | 8
Q | garage &tools | Ready-Lite | 200 | 6
R | external mech rm 112 | Beghelli | 150 | 5
R | 2nd floor mech rm 212 | Beghelli | 150 | 5
R | external mech rm 150 | Beghelli | 150 | 3
R | main elec rm 137 | Beghelli | 360 | 7
R | main elec rm 137 | Beghelli | 200 | 5
R | main elec rm 137 | Beghelli | 200 | 3
House # 1 | liv rm | Stanpro SLA-2L | 36 | 0
House # 2 | liv rm | Stanpro SLA-2L | 36 | 0
House # 3 | liv rm | Stanpro SLA-2L | 36 | 0
House # 4 | liv rm | Stanpro SLA-2L | 36 | 0
House # 5 | din rm | Stanpro SLA-2L | 36 | 0
House # 6 | din rm | Stanpro SLA-2L | 36 | 0
House # 7 | din rm | Stanpro SLA-2L | 36 | 0
House # 8 | din rm | Stanpro SLA-2L | 36 | 0
House # 9 | din rm | Stanpro SLA-2L | 36 | 0
House # 10 | Bed rm/hallways | Luma-cell | 200 | 0
House # 10 | Entrance/laundry | Luma-cell | 200 | 3
House # 11 | Bed rm/hallways | Luma-cell | 200 | 3
House # 11 | Entrance/laundry | Luma-cell | 200 | 3
Total | 51 |  |  | 174

## Aspect # 4
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 4: Fire Extinguishers/Exit lights on battery
Type | ABC | K-guard | All exit lights on battery
BUILDING | Qty | Qty | None on site
A | 9 |  | 0
B | 5 |  | 0
C | 2 | 1 | 0
D | 4 |  | 0
E | 6 |  | 0
F | 9 |  | 0
G | 4 |  | 0
H | 2 |  | 0
I | 1 |  | 0
J | 5 |  | 0
K | 3 |  | 0
L | 2 |  | 0
P | 5 |  | 0
Q | 10 |  | 0
Q- spares | 11 |  | 0
R | 18 |  | 0
Housing 01 | 1 |  | 0
Housing 02 | 1 |  | 0
Housing 03 | 1 |  | 0
Housing 04 | 1 |  | 0
Housing 05 | 1 |  | 0
Housing 06 | 1 |  | 0
Housing 07 | 1 |  | 0
Housing 08 | 1 |  | 0
Housing 09 | 1 |  | 0
Housing 10 | 1 |  | 0
Housing 11 | 1 |  | 0
TOTAL | 107 | 2 | 0

## Aspect # 5
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 5: Fire Hydrants
Equipment | Hydrant only |  | All Hydrants require Dechlorination during flow testing and/or flushing
Location on site | Make | Type | High risk to environment -Dechlorinate
S/East of House 4 | Canadian Valve |  | dechlorinate
West of Building F | Canadian Valve |  | dechlorinate
N/West of Building B | Canadian Valve |  | dechlorinate
East of Building D | Terminal City |  | dechlorinate
South of Building A | Terminal City |  | dechlorinate
East of Building Q | Terminal City |  | dechlorinate
West of Building R | ?? |  | dechlorinate
TOTAL | 7 |  | 7

## Aspect # 6
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 6: Back Flow Preventers
| Domestic water | Fire | Confined space
BUILDING | Qty | Qty | YES or NO
A | 1 | 1 | No
B |  | 1 | No
E | 1 | 1 | No
F | 2 | 1 | No
G |  | 1 | No
J | 1 |  | No
P | 2 | 1 | No
Q | 1 | 1 | No
R | 1 | 2 | No
Housing 10 |  | 1 | No
Housing 11 |  | 1 | No
TOTAL | 8 | 11

## Aspect # 7
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 7: Standpipe/Hose Cabinet systems (occupant use hose)
Material,class, type | Canvass | Class-qty of each class of system in each building | Type of standpipe and qty of each type per bldg | Length of standpipe HOSES
BUILDING | QTY | Class 1, 2 or 3 | eg.automatic/ dry/manual/wet/ semi-automatic dry | Length in feet
E | 1 | 2 | automatic | 1" - 100 feet

## Aspect # 8
FRASER VALLEY INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 8: Kitchen Sprinkler Suppression systems
EQUIPMENT | Bldg C
Make | Kidde
Model | WHDR 600
Actuation type | mechanical
Number of cylinders | 1
Number of nozzles | 6
Number of suppression system fusible links | 7
Size of cylinders | 1 - 6 gallon
Fire damper assembly type | none
Fire damper assembly fusible links to replace | none