## Aspect # 1
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 1: Fire alarm system/devices
Device | main alarm panel | anunciator panel | manual pull station | manual pull station-2stage | smoke detector | smoke detector | Combo smoke and heat | smoke alarm | heat detector RHT | Combo smoke/heat-RHT | pressure switch | pressure switch alarm | pressure switch | flow switch | tamper switch | strobe | horn with strobe | buzzer/chime | bell | G/A | ancilliary device | end of line resistor
Type |  |  |  |  | duct | photo or ion | ion or photo/heat |  | rate of rise |  | low water | main | low air
BUILDING | Make/Stage | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty
Administration (N, VC, PC, AD,HC, R) | 1- Edwards EST-3 two stage |  | 5 |  | 8 | 11 |  |  |  | 11 |  |  |  | 6 | 6 | 2 |  | 1 | 7 | 5
A-B | covered by admin panel |  | 1 |  | 4 | 4 |  |  |  | 80 | 1 | 1 |  | 5 | 10 |  |  | 2 | 1 | 1
C-D | covered by admin panel |  | 1 |  | 4 |  |  |  |  | 81 |  |  |  | 4 | 7 |  |  | 2 | 2 | 1
E-F | covered by admin panel |  | 1 |  | 4 |  |  |  | 3 | 82 |  |  |  | 4 | 8 |  |  | 1 | 1 | 1
G-H | covered by admin panel |  | 1 |  | 4 | 2 |  |  | 4 | 78 |  |  |  | 5 | 9 |  |  | 1 | 1 | 1
Q | covered by admin panel |  | 1 | [15 empty] | 4 | 1 | 1
W-X | covered by admin panel | [12 empty] | 1 | 1 |  |  |  | 2
AC | covered by admin panel |  | 1 |  |  | 4 | [7 empty] | 1 | 1 | 1 |  |  | 3 | 1
CS-L-S | covered by admin panel |  |  |  | 4 | [13 empty] | 4
V | covered by admin panel |  |  |  | 9 | [6 empty] | 1 | 1 | 1 | 2 | 2 |  | 2 | 7
R | covered by admin panel | [5 empty] | 2 | [6 empty] | 1 | 1 |  |  |  | 3
J-K | covered by admin panel |  | 1 |  | 4 |  |  |  | 6 | 63 | 1 | 1 |  | 3 | 16 |  |  | 1 | 4 | 1
FE-PS-UCCO | covered by admin panel | [7 empty] | 2
GO | 1- Edwards EST 3 - 1 stage |  | 9 |  | 1 |  | 6 |  | 1 | 1 | [6 empty] | 12 |  |  |  |  | 1
PE | 1- Edwards EST 2 - 1 stage |  | 2 |  |  | 5 | [7 empty] | 1 | 1 |  |  |  | 2
POD1 | 1- Edwards EST 3 - 2 stage |  |  | 15 | 2 | 114 |  |  |  | 34 |  | 1 |  | 14 | 28 |  | 35
POD2 | 1- Edwards EST 3 - 2 stage | 1 |  | 15 | 3 | 96 |  |  |  | 60 |  | 1 |  | 13 | 28 |  | 32
PWRH | 1- Edwards EST 3 - 1 stage |  | 3 |  |  | 2 |  |  | 1 | 1 | [5 empty] | 2 |  |  | 2
PMPH | covered by pwrh panel |  | 1 |  |  | 1 | [8 empty] | 4
ST | 1- Edwards EST 1 - 1 stage |  | 2 | [10 empty] | 1 | 1 |  |  |  | 1 |  |  | 1
PFV 1 | covered by admin panel | [6 empty] | 4
PFV 2 | covered by admin panel | [6 empty] | 4
PFV 3 | covered by admin panel | [6 empty] | 4
TOTAL | 7 | 1 | 29 | 30 | 47 | 239 | 8 | 12 | 17 | 491 | 2 | 5 | 1 | 76 | 123 | 7 | 79 | 10 | 44 | 12 | 1 | 2
(see aspect #9 for 96 more smoke test points in both POD 1 and POD 2 via the VESDA system)
10

## Aspect # 2
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 2: Sprinkler systems/trees
Component | Dry sprinkler system | Wet sprinkler system | Fire dept connections
BUILDING | Qty | Qty | Qty
MAIN | 1 | 2- (covering 16 areas in main bldg)
GO |  | 2 | 1
PE |  | 1
POD1 |  | 1
POD2 |  | 1
ST |  | 1 | 3
TOTALS | 1 | 8 | 4
Total # of gauges on site for each type of sprinkler system | 3 | 117

## Aspect # 3
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 3: Emergency Lighting
BUILDING | Location | Make | Watts | # of remote heads
GO | front entrance | Readylite | 100 | 3
GO | training rm | Readylite | 144 | 3
GO | mech rm 206 | Readylite | 100 | 2
GO | comm rm 205 | Readylite | 144 | 2
GO | elec rm 107 | Readylite | 144 | 3
GO | s stairwell bottom | Readylite | 144 | 3
GO | n stairwell bottom | Readylite | 144 | 3
PWRH | / | Lumacell | 200 | 1
PMPH | / | Lumacell | 360 | 1
PE | front entrance | Readylite | 36 | 0
PE | control rm/bubble | Readylite | 36 | 0
PE | 2nd floor above elevator | Stanpro | 36 | 0
PE | smo office | Readylite | 100 | 0
MAIN | agda | Readylite | 36 | 0
MAIN | by v&c | Readylite | 36 | 0
MAIN | by v&c | Readylite | 36 | 0
MAIN | admin lower | Readylite | 144 | 4
MAIN | n admin stair | Readylite | 36 | 0
MAIN | s admin stair | Readylite | 36 | 0
MAIN | admin | Lumacell | 36 | 0
MAIN | admin | Lumacell | 36 | 0
MAIN | CER | Readylite |  | 4
MAIN | admin stair to tunnel | Readylite | 36 | 6
MAIN | gym gun walk | Readylite | 72 | 0
MAIN | J/K mechanical | Central power system | 34 | 17
MAIN | across from chapel | Readylite | 100 | 0
MAIN | across from ops office | Readylite | 160 | 0
MAIN | a&d | Beghelli | 150 | 5
MAIN | library office | Emergilite | 36 | 0
MAIN | elevator (on top of) | Emergilite | 36 | 0
MAIN | hosp pharmacy | Lumacell | 36 | 0
MAIN | hosp by pharmacy | Lumacell | 72 | 0
MAIN | hosp by HC 118 | Readylite | 100 | 0
MAIN | hosp by nurses station | Readylite | 100 | 0
MAIN | hosp # 14 | Readylite | 36 | 0
MAIN | hosp # 13 | Lumacell | 36 | 0
MAIN | gym office | Readylite | 36 | 0
MAIN | J/K corridor | Readylite | 36 | 0
MAIN | K office | Readylite | 36 | 0
MAIN | J office | Readylite | 36 | 0
MAIN | hosp control | Lumacell | 36 | 0
MAIN | tunnel G/H door | Lumacell | 36 | 0
MAIN | tunnel G/H | Stanpro | 180 | 12
MAIN | tunnel E/F door | Readylite | 36 | 0
MAIN | tunnel E/F | Readylite | 150 | 12
MAIN | kitchen control | Readylite | 36 | 0
MAIN | kitchen gun walk | Lumacell | 100 | 0
MAIN | kitchen gun walk | Lumacell | 36 | 1
MAIN | Tunnel C/D door | Readylite | 36 | 0
MAIN | Tunnel C/D | Stanpro | 180 | 12
MAIN | Tunnel A/B door | Readylite | 36 | 0
MAIN | Tunnel A/B | Readylite | 150 | 12
MAIN | Tunnel by sewage | Stanpro | 36 | 0
MAIN | Tunnel by kitchen control | Readylite | 36 | 0
MAIN | kitchen | Readylite | 36 | 0
MAIN | kitchen | Readylite | 36 | 0
MAIN | sacred services office | Lumacell | 200 | 8
MAIN | 2nd floor office closet | edwards | 360 | 11
MAIN | iss | unicell | 100 | 0
MAIN | laundry | Lumacell | 36 | 0
MAIN | iss | unicell | 36 | 0
MAIN | maint | Readylite | 36 | 0
MAIN | boiler rm top of breakers | Readylite | 36 | 0
POD 1 | lunchroom | Lumacell | 360 | 4
POD 1 | gun walk elec E7-4 | Readylite | 360 | 14
POD 1 | gun walk elec E5-15 | Readylite | 360 | 6
POD 2 | gun walk elec top | Lumacell | 360 | 8
POD 2 | gun walk elec bottom | Lumacell | 360 | 4
POD 2 | gun walk elec top | Lumacell | 360 | 5
POD 2 | gun walk elec bottom | Lumacell | 360 | 8
Total | 69 |  |  | 144

## Aspect # 4
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 4: Fire Extinguishers/Exit lights on battery
Type | ABC | CO2 | K-guard | All exit lights on battery
BUILDING | Qty | Qty | Qty | Qty
MAIN | 139 | 3 | 1 | 0
GO | 6 |  |  | 16
COMP | 1 |  |  | 0
PE | 5 |  |  | 0
PFV1 | 1 |  |  | 0
PFV2 | 1 |  |  | 0
PFV3 | 1 |  |  | 0
PFV stor | 1 |  |  | 0
SWT | 1 |  |  | 0
PMPH | 2 |  |  | 0
POD1 | 19 |  |  | 0
POD2 | 25/5 spares |  |  | 0
PWRH | 2 |  |  | 0
ST | 4 |  |  | 0
vehicles/equipment | 9 |  |  | 0
Towers | 4 |  |  | 0
spares | 2 | 5 |  | 0
Public works | 1 |  |  | 0
Gas pumps | 2 |  |  | 0
MS | 1 |  |  | 0
VS | 3 |  |  | 0
TOTAL | 235 | 8 | 1 | 16

## Aspect # 5
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 5: Fire Hydrants
Equipment | Hydrant only |  | All Hydrants require Dechlorination during flow testing and/or flushing
Location on site | Make | Type | High risk to environment -Dechlorinate
By segregation | Terminal City | C71P | dechlorinate
Behind A & B | Terminal City | C71P | dechlorinate
Behind H yard | Terminal City | C71P | dechlorinate
Behind G yard | Terminal City | C71P | dechlorinate
ISS | Terminal City | C71P | dechlorinate
Maintenance | Terminal City | C71P | dechlorinate
Kitchen | Terminal City | C71P | dechlorinate
2 lift station gate | Terminal City | C71P | dechlorinate
By B yard | Terminal City | C71P | dechlorinate
10 sport field | Century Mueller | Canada Valve | dechlorinate
Rear POD 2 | Century Mueller | Canada Valve | dechlorinate
Rear POD 1 | Terminal City | C71P | dechlorinate
GO bldg | Terminal City | C71P | dechlorinate
Pump house | Century Mueller | Canada Valve | dechlorinate
TOTAL | 14 |  | 14

## Aspect # 6
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 6: Back Flow Preventers
| Domestic water | Fire | Confined space
BUILDING | Qty | Qty | YES or NO
A-B | 1 |  | No
C-D | 1 |  | No
E-F | 1 |  | No
G-H | 1 |  | No
GO | 2 | 1 | No
PE |  | 1 | No
PMPH | 1 | 5 | No
North mech PC bldg | 1 |  | No
Upper V mr | 1
POD1 | 1 | 1 | Yes
POD2 | 2 | 1 | No
CS-L-S | 1 |  | No
Q | 9 |  | No
V -south mech rm | 2 |  | No
TOTAL | 24 | 9

## Aspect # 7
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 7: Standpipe/Hose Cabinet systems. (occupant use hose)
Material,class, type and demand | Nylon | Class-qty of each class of system in each building | Type of standpipe and qty of each type per bldg | Standpipe system design demand | Length of standpipe HOSES
BUILDING | QTY | Class 1, 2 or 3 | eg.automatic/ dry/manual/wet/ semi-automatic dry | GPM - L/min | Length in feet
A-B | 5 plus 4 extensions | 4-class 2, 1-class 3 | All Automatic |  | 5@75 ft, 4 ext @50 ft,
C-D | 5 plus 4 extensions | 4-class 2, 1-class 3 | All Automatic |  | 5@75 ft, 4 ext @50 ft,
E-F | 5 plus 4 extensions | 4-class 2, 1-class 3 | All Automatic |  | 5@75 ft, 4 ext @50 ft,
G-H | 5 plus 4 extensions | 4-class 2, 1-class 3 | All Automatic |  | 5@75 ft, 4 ext @50 ft,
HC | 2 | class 2 | All Automatic |  | 2@75 ft
N | 1 | class 2 | All Automatic |  | 1@75 ft
N-north mech | 1 | class 2 | All Automatic |  | 1@75 ft
PC | 1 | class 2 | All Automatic |  | 1@75 ft
POD1 | 14 plus 10 extensions | class 2 | All Automatic |  | 14@100 ft, 10 ext @75 ft,
POD2 | 14 plus 10 extensions | class 2 | All Automatic |  | 14@100 ft, 10 ext @75 ft,
R | 2 | class 2 | All Automatic |  | 2@75 ft
TOTAL | 55

## Aspect # 8
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 8: Kitchen Sprinkler Suppression systems
EQUIPMENT | Q-main
Make | Kidde
Model | Wet chem
Actuation type | mechanical
Number of cylinders | 1
Number of nozzles | 7
Number of suppression system fusible links | 6
Size of cylinders | 6 gal
Fire damper assembly type | 2 dampers in each hood
Fire damper assembly fusible links to replace | 2 links in each hood- 4 total

## Aspect # 9
KENT INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 9: Vesda smoke alarm system
Component | main alarm panel | Fire works Panel | Key pad | Vesda controller | Annunciator | Sample Points | Comments
Device type/model |  |  |  | Xtralis VLS-300
BUILDING | Qty/Make | Qty | Qty | Qty | Qty | Qty
Pod 1 | 1-Edwards EST3 | 1 | 4 | 24 | 0 | 96 | Veasda sampling points are in the inmate cell exhaust duct.
Pod 2 | 1-Edwards EST3 | 1 | 1 | 24 | 1 | 96 | Veasda sampling points are in the inmate cell exhaust duct.