## Aspect # 1
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 1: Fire alarm system/devices
Device | main alarm panel | Nodes | combo LCD/LED annunciator panel | manual pull station | smoke/CO/ sounder base | smoke detector | smoke detector | smoke/sounder base detector | 2 -1/2 min timer points in panel to be verified - applies only to inmate housing A1 - A23 smokes | heat detector | heat detector | relay | piezo | flow switch | tamper switch | horn/visual alarm | EOL | isolator | kitchen hood device | generic monitor | visual alarm
Type | Main system annunciator in bldg 1 and network annunciator work station in bldg 24. Bldg panels have built in annunciators. |  |  |  |  | duct | photo or ion |  | no timers for mech room smokes - one MR per bldg | fixed temp | rate of rise
BUILDING | Make/Stage | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty
1 | Simplex model 4007ES single stage | 1 -NDU Node 40 model 4100ES | 1 | 5 |  |  | 7 | [6 empty] | 1 | 2 | 6 | 3 | 1
2 | Simplex model 4007ES single stage |  |  | 4 | [9 empty] | 1 | 2 | 3 | 3 | 1
3 | Simplex model 4007ES single stage |  |  | 10 |  |  | 6 | [6 empty] | 1 | 4 | 7 | 5 | 1 | 1 | 1 | 1
4 | Simplex model 4007ES single stage |  |  | 4 | [6 empty] | 7 |  |  |  |  | 2 |  | 1
10 | Simplex model 4007ES single stage |  |  | 2 | [6 empty] | 3 |  |  |  |  | 1
14 | Simplex model 4007ES single stage |  |  | 1 | [6 empty] | 2 |  |  |  |  | 1 | 1 | 1
18 | Simplex model 4007ES single stage |  |  | 1 | [6 empty] | 4 | [5 empty] | 1 | 1
20/20A | Simplex model 4007ES single stage |  |  | 5 | [6 empty] | 11 |  |  |  |  | 2-bldg 20 |  | 1-bldg 20
21 | Simplex model 4007ES single stage |  |  | 5 |  | 1 |  |  |  |  | 1 |  |  | 3 | 7 |  | 10 | 3
23 | Simplex model 4007ES single stage |  |  | 2 | [6 empty] | 10 | [6 empty] | 1
24 | Simplex model 4007ES single stage |  |  | 3 | [6 empty] | 7 | [6 empty] | 1
27 | Simplex model 4007ES single stage |  |  | 3 | [6 empty] | 9 |  |  | 1 | 3 | 1 | 4 | 1
28 | Simplex model 4007ES single stage |  |  | 3 | [5 empty] | 8 | [5 empty] | 2 | 1
29a | Simplex model 4007ES single stage |  |  | 1 | 2 |  |  | 4 | [7 empty] | 1 | 1 |  |  |  | 3
29b | Simplex model 4007ES single stage |  |  | 2 | 1 |  |  | 4 | [7 empty] | 1 | 1
34 | Simplex model 4007ES single stage |  |  | 3 | [5 empty] | 7 | [5 empty] | 1 | 1
35 | Simplex model 4007ES single stage |  |  | 3 | [6 empty] | 3 |  |  |  |  | 2 | 1
44 | On bldg 3 panel |  |  | 3 | [5 empty] | 2 | [7 empty] | 1
A1 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A2 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A3 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A4 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A5 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A6 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A7 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A8 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 6 | 8 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A9 | Simplex model 4007ES single stage |  |  | 3 | 3 |  |  | 7 | 9 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A10 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 8 | 10 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A11 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 8 | 10 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A12 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 | 1 | 4
A13 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 |  | 4 | 1
A14 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 | 1 | 4
A15 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 |  | 4 | 1
A16 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 8 | 10 |  |  |  |  | 1 | 3 | 1 | 4
A17 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  | 3 | 1 | 3 | 1 | 4
A18 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 8 | 10 |  |  |  |  | 1 | 3 | 1 | 4
A19 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 | 1 | 4 | 1
A20 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 4 | 6 |  |  |  |  | 1 | 3 | 1 | 4
A21 | Simplex model 4007ES single stage |  |  | 2 | 2 |  |  | 11 | 12 |  |  |  |  | 1 | 3 | 2 | 4 | 1
A22 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 11 | 13 |  |  |  |  | 1 | 3 |  | 4 | 1
A23 | Simplex model 4007ES single stage |  |  | 2 | 3 |  |  | 9 | 11 |  |  |  |  | 1 | 3 | 1 | 4 | 1
LU24 | Simplex model 4007ES single stage |  | 1 | 16 | 25 |  | 95 |  | 0 |  | 1 | 11 |  | 11 | 17 | 23 | 28 | 16
TOTAL | 41 | 1 | 2 | 123 | 96 | 1 | 108 | 154 | 191 | 17 | 58 | 11 | 3 | 41 | 104 | 85 | 152 | 47 | 1 | 1 | 4

## Aspect # 2
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 2: Sprinkler systems/trees
Component | Dry sprinkler system | Wet sprinkler system | check valve | water motor gong | Fire hose valve | compressor for dry system if applicable | flow valve | shut off valve | Fire dept connections
BUILDING | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty | Qty
1 |  | 1 | 2 |  | 2 |  | 1 | 2 | 1
2 |  | 1 | 2 |  | 2 |  | 1 | 2 | 1
10 | [8 empty] | 1
3 |  | 1 | 2 |  | 2 |  | 1 | 2 | 1
21 | 1 partial | 1 partial | 2 | 1 | 2 | 1 | 2 | 3
27 |  | 1 | 1 |  |  |  | 1 | 2
A1-A23 |  | 23
LU24 | 1 partial | 4 | 2 |  |  | 1 | 4 | 9 | 1
TOTALS | 2 | 32 | 11 | 1 | 8 | 2 | 10 | 20 | 5
Total # of gauges on site for each type of sprinkler system | 5 | 46

## Aspect # 3
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 3: Emergency Lighting
BUILDING | Location | Make | Watts | # of remote heads
House 1 | n/a | ready-lite | 36 | 0
House 2 | n/a | ready-lite | 36 | 0
House 3 | n/a | lumacell | 72 | 0
House 4 | n/a | lithonia | 36 | 0
House 5 | n/a | ready-lite | 36 | 0
House 6 | n/a | lumacell | 36 | 0
House 7 | n/a | ready-lite | 36 | 0
House 8 | n/a | lumacell | 36 | 0
House 9 | n/a | lumacell | 72 | 0
House 10 | by A10-15A | stanpro | 36 | 0
House 10 | by A10-14 | edwards | 36 | 0
House 10 | by A10-3 | stanpro | 36 | 0
House 11 | by A11-15A | edwards | 230 | 0
House 11 | by A11-3 | edwards | 36 | 0
House 11 | by A 11-11 | edwards | 36 | 0
House 12 | n/a | ready-lite | 36 | 0
House 13 | n/a | stanpro | 100 | 0
House 14 | n/a | dualite | 250 | 0
House 15 | n/a | lithonia | 100 | 0
House 16 | n/a | edwards | 220 | 0
House 16 | by A16-4 | edwards | 36 | 0
House 16 | by A16-11 | edwards | 36 | 0
House 17 | n/a | stanpro | 72 | 0
House 18 | n/a | ready-lite | 36 | 0
House 18 | by 133 | edwards | 36 | 0
House 18 | by 138 | edwards | 36 | 0
House 19 | n/a | stanpro | 250 | 0
House 20 | n/a | lumacell | 36 | 0
House 21 | n/a | beghelli | 80 | 0
House 22 | n/a | ready-lite | 36 | 0
House 23 | n/a | dualite | 216 | 0
1 | admin mech rm 1 | stanpro | 72 | 2
1 | admin mech rm 2 | stanpro | 72 | 2
1 | admin mech rm 3 | stanpro | 160 | 2
1 | admin mech rm 4 | dualite | 160 | 2
1 | admin mech rm 5 | dualite | 350 | 11
2 | activities bldg progs elec | dualite | 350 | 10
2 | activities bldg progs elec | stanpro | 36 | 0
3 / EAA 1 | inst services 3-11 | dualite | 216 | 0
3/ EAA1 | inst services 3-13 | stanpro | 216 | 2
3 / EAB 3 | inst services 3-15 | dualite | 216 | 0
3/ EAA 1 | inst services 3-23 | stanpro | 36 | 0
3 / EAA 1 | inst services 3-24 | beghelli | 360 | 0
3 / EAA 1 | inst services 3-26 | dualite | 216 | 4
3 / EAA 4 | inst services 3-27 | dualite | 216 | 4
3 | inst services 3-27 | dualite | 216 | 0
3 /EAA 3 | inst services 3-30 | stanpro | 250 | 2
3 | kitchen | dualite | 216 | 0
10 | carpentry above 10-2 | ready-lite | 36 | 0
10 | carpentry above 10-3 | ready-lite | 36 | 0
16 (8) EM-1 | electrical room | ready-lite | 36 | 0
20 | health services storage | stanpro | 72 | 0
20a | health services | edwards | 360 | 14
21 | textiles 1st floor storage | ready-lite | 250 | 10
21 | textiles 2nd floor | ready-lite | 250 | 12
23 | chapel entrance | lumacell | 36 | 0
23 | chapel north | Stanpro | 36 | 0
23 | chapel south | Stanpro | 36 | 0
24 | multi purpose south | lumacell | 36 | 0
24 | multi purpose north | lumacell | 36 | 0
27 | psychology | stanpro | 100 | 0
28 | equip shed 3a-stair | ready-lite | 36 | 0
28 | equip shed 3a | lumacell | 36 | 0
35 | workshop 35-1 | stanpro | 36 | 0
35 | workshop 35-2 | ready-lite | 36 | 0
35 | workshop 35-3 | beghelli | 40 | 0
LU 24 | bsmt south corridor next to stair 1 | lumacell | 200 | 0
LU 24 | bsmt west corridor next to stair 2 | lumacell | 200 | 0
LU 24 | bsmt east corridor next to stair 3 | lumacell | 200 | 0
LU 24 | bsmt elec rm 016 | lumacell | 350 | 0
LU 24 | ground floor west mech rm w110 | lumacell | 150 | 0
LU 24 | ground floor north mech rm n110 | lumacell | 150 | 0
LU 24 | ground floor east mech rm e110 | lumacell | 150 | 0
LU 24 | ground floor storage rm 119 | lumacell | 200 | 0
LU 24 | second floor west mech rm w209 | lumacell | 150 | 0
LU 24 | second floor north mech rm n211 | lumacell | 150 | 0
LU 24 | second floor east mech rm e209 | lumacell | 150 | 0
LU 24 | south meeting rm 206 | lumacell | 250 | 0
Total | 78 |  |  | 77

## Aspect # 4
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 4: Fire Extinguishers/Exit lights on battery
Type | ABC | CO2 | K-guard | BC | All exit lights on battery
BUILDING | Qty | Qty | Qty | Qty | Qty
1 | 6 | 1 |  |  | 7
2 | 5 |  |  |  | 5
3 | 3 |  | 2 |  | 9
4 | 1
10 | 2
10a
14 | 1
18 | 1 and 10 spares
20 | 5
20a
21 | 5 |  |  | 1 | 6
23 | 1
24 | 1
25 | 1
27
28 | 3 |  |  |  | 1
29a | 2
29b | 2
30 | 2 |  |  | 1
31 | 1
34 | 3 |  |  | 1
35 | 3 and 1 spare and 2 on forklift and backhoe |  |  |  | 3
36
37 | 2
38 | 1
39 | 1
40
41
42
43
44 | 1
A1-A23 | 23
LU24 | 19 |  |  |  | 22
TOTAL | 108 | 1 | 2 | 3 | 53

## Aspect # 5
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 5: Fire Hydrants
Equipment | Hydrant only |  | All Hydrants require Dechlorination during flow testing and/or flushing
Location on site | Make | Type | High risk to environment -Dechlorinate
south side of north access road-behind A13 | #11 Century | FM | dechlorinate
behind house A8 | #6 Century | FM | dechlorinate
in between house A7 and A12 | #7 Century | FM | dechlorinate
at LU 24 | #8 Terminal City | C71P | dechlorinate
beside house A17 | # 10 Century | FM | dechlorinate
beside house A6 | #3 Century | FM | dechlorinate
east of pond edge of gravel road | #9 Century | FM | dechlorinate
between phone box and gazebo | #2 Century | Darling | dechlorinate
beside house A22 | #5 Century | FM | dechlorinate
south end of bldg 3 | #1 Century | FM | dechlorinate
beside fuel tanks | #4 Century | FM | dechlorinate
composter | #13 Century Mueller | FM | dechlorinate
at entrance to property main road | Terminal City Iron | 150 WP | dechlorinate
NEW between sports field / Native grnds. | Century Mueller | FM | dechlorinate
TOTAL | 14 |  | 14

## Aspect # 6
MISSION MINIMUM INSTITUTION
FIRE PROTECTION SYSTEMS - ASPECT # 6: Back Flow Preventers
| Domestic water | Fire | Confined space
BUILDING | Qty | Qty | YES or NO
1 | 1 | 1 | NO
2 | 1 | 1 | NO
3 |  | 1 | NO
20 | 1 |  | NO
21 |  | 1 | NO
27 |  | 1 | NO
LU 24 | 2 | 1 | NO
House A1 |  | 1 | NO
House A2 |  | 1 | NO
House A3 |  | 1 | NO
House A4 |  | 1 | NO
House A5 |  | 1 | NO
House A6 |  | 1 | NO
House A7 |  | 1 | NO
House A8 |  | 1 | NO
House A9 |  | 1 | NO
House A10 |  | 1 | NO
House A11 |  | 1 | NO
House A12 |  | 1 | NO
House A13 |  | 1 | NO
House A14 |  | 1 | NO
House A15 |  | 1 | NO
House A16 |  | 1 | NO
House A17 |  | 1 | NO
House A18 |  | 1 | NO
House A19 |  | 1 | NO
House A20 |  | 1 | NO
House A21 |  | 1 | NO
House A22 |  | 1 | NO
House A23 |  | 1 | NO
TOTAL | 5 | 29